## Slide 1: Simulation of Transport of Synchronization over a Network of Enhanced PTP and Enhanced SyncE Clocks November 6, 2018
Geoffrey Garner
Jingfei Lv
Michael Mayer

## Slide 2: Introduction
ITU-T SG 15, Q13 is developing standards to support timing requirements for 5G
  Expected to be more stringent than current requirements for LTE-TDD
  Standards will include requirements for enhanced SyncE and PTP clocks
The development process includes
  Time error allocations for each source of error (budgeting)
  Development of HRMs
  Simulations for budget components that include effect of random noise, timestamp granularity, and SyncE and PTP rearrangements (transients)
This presentation describes this work, with focus on the simulation work
Caveats
  This presentation does not reflect all conclusions at the 8 – 19 October 2018 Q13/15 meeting
  There is a minimum of background material (it is assumed that this can be obtained from the references at the end of this presentation and the tutorials )

## Slide 3: Outline
Introduction (previous slide)
End-to-end application requirements
Budgeting
Enhanced clocks
Hypothetical Reference Models (HRMs)
Assumptions needed for enhanced clocks
Simulation results
Conclusions and Future Work
References
Backup
  Simulation model
  Additional simulation results
  Stability considerations

## Slide 4: End-to-End Requirements
Existing requirement for LTE-TDD
  max|TE| of 1.5 𝜇s for Rec. G.8271, Table 1, Level of Accuracy 4
Requirements for 5G (see [1])
  max|TE| of 1.5 𝜇s for 5G TDD service, from Rec. G.8271
  Requirements for additional use-cases are under development, and at least some are expected to be more stringent than 1.5 𝜇s max|TE|
  Cluster-based synchronization requirements (see Table 2/G.8271)
    260 ns maximum relative time error (i.e., TAE) for Level of Accuracy 6A (includes intra-band non-contiguous CA and inter-band CA)
    130 ns TAE for Level of Accuracy 6B (intra-band contiguous CA)
    65 ns TAE for Level of Accuracy 6C (for MIMO or TX diversity transmissions at each carrier frequency)

## Slide 5: Budgeting
Based on previous work for LTE-TDD, sources of time error include (see [2])
  PRTC
  Dynamic time error (dTE), i.e., effect of random SyncE noise, PTP timestamp granularity, and SyncE rearrangements
  Constant time error (cTE), both in node and link
  Effect of holdover and rearrangements in the network (PTP)
  Effect of holdover and rearrangements in the end application
  End application (other than holdover and rearrangements)
Not all components are present in all scenarios
The focus for simulations, in this presentation, is on b)

## Slide 6: Enhanced Clocks
Enhanced Ethernet Equipment Clock (eEEC)
Telecom Boundary Clock Class C (T-BC-C)
Telecom Boundary Clock Class D (T-BC-D)
Telecom Time Slave Clock Class C (T-TSC-C)
Telecom Time Slave Clock Class D (T-TSC-D)
Enhanced PRTC (ePRTC) – not needed for cases described here
Enhanced PRC (ePRC) – not needed for cases described here
Distinction between T-BC and T-TSC classes C and D not needed for cases described here

## Slide 7: Hypothetical Reference Models – 1
7 enhanced HRMs (eHRMs) were developed in Q13/15
  They are documented in the Q13/15 document WDeTSS [3]
  Additional HRMs are under development for cluster-based synchronization
The simulations focused on the following two HRMs (see following slides), where the enhanced SyncE and PTP transport take the same path (congruent case)
  Previous experience with simulations for non-enhanced clocks indicated the congruent case is most conservative from the standpoint of SyncE transients, because in this case a SyncE transient affects all the PTP clocks (as opposed to only a subset)

## Slide 8: Hypothetical Reference Models – 1
eHRMa (taken from Figure 1 of [3])

## Slide 9: Hypothetical Reference Models – 1
eHRMc (taken from Figure 1 of [3])

## Slide 10: Assumptions Needed for Enhanced Clocks
eEEC noise generation and transfer (see [3]; these are working assumptions for simulations)
  TDEV mask has same shape as EEC TDEV mask, but amplitude is reduced by factor of 0.2
  MTIE mask level approximately 0.25 of EEC MTIE mask
  1 – 3 Hz bandwidth, 0.2 dB maximum gain peaking
eEEC transients (simulated ranges of parameters)
  Transient modeled as standard ring reconfiguration using SSMs (msg timers consistent with [4]
  Initial phase step: 5 ns, 10 ns (with mitigation, see below, also looked at larger steps)
  Initial frequency offset: 1 ppb, 5 ppb, 10 ppb
  Considered cases with and without mitigation by turning off the T-BC filtering during the transient (detected via the SSMs)
T-BC noise transfer: 0.05 Hz – 0.1 Hz bandwidth, 0.1 dB gain peaking
Results include 0.1 Hz first-order, low-pass measurement filter
Other parameters/assumptions consistent with [5]

## Slide 11: eHRMa Results – no SyncE transients
Node 0 is 1st T-BC
Node 20 is T-TSC
8 ns timestamp granularity
0.1 Hz T-BC and T-TSC filters
Unfiltered max|TE| within 50 ns
0.1 Hz Low-pass filtered max|TE| within 40 ns

## Slide 12: eHRMc Results – no SyncE transients
Node 0 is 1st T-BC
Node 10 is T-TSC
8 ns timestamp granularity
0.1 Hz T-BC and T-TSC filters
Unfiltered max|TE| within 46 ns
0.1 Hz Low-pass filtered max|TE| within 30 ns
Max|TE| increases more rapidly over last 3 nodes because these contain non-enhanced clocks

## Slide 13: eHRMa Results – SyncE transients only
No mitigation
All results with 0.1 Hz low-pass measurement filter
Node 0 is 1st T-BC
Node 20 is T-TSC
Filtered max|TE| within 50 ns objective (see [3]) for all cases with 1 ppb frequency offset, and for 5 ppb offset with 0.1 Hz filters and 5 ns phase step

## Slide 14: eHRMa Results – SyncE transients only
Mitigation by turning off T-BC filtering during transient
All results with 0.1 Hz low-pass measurement filter
Node 0 is 1st T-BC
Node 20 is T-TSC
Filtered max|TE| within 50 ns objective (see [3]) for 10 ppb frequency offset and 5, 10, or 15 ns phase step

## Slide 15: Conclusions and Future Work
max|TE| measured through 0.1 Hz low-pass measurement filter, due to eSyncE noise and timestamp granularity, is within 40 ns for 20 T-BCs (eHRMa) and 30 ns for 10 T-BCs (with last 3 nodes non-enhanced); results slightly larger for 0.05 Hz filters
max|TE| due to SyncE transients can be kept within the 50 ns objective of [3]
  If mitigation by turning off the T-BC filters is used, can increase transient frequency offset that can be tolerated from 1 ppb (or 5 ppb in limited cases) to 10 ppb, and can increase phase offset from 5 or 10 ns to 15 ns
Total max|TE| is, at most, additive; therefore, total max|TE| due to random effects plus SyncE transients can be kept to within 100 ns
These results are a significant improvement over the non-enhanced cases, where total max|TE| was kept to within 200 ns for 11 nodes.
Several possible future work items
  Develop eHRMs for cluster-based synchronization and simulate TE accumulation for these cases
  Consider mitigation by rejecting the SyncE transient (this scheme can be used with non-enhanced SyncE (this scheme is allowed for non-enhanced SyncE, see [7])

## Slide 16: References – 1
[1] ITU-T Recommendation G.8271/Y1366, Time and phase synchronization aspects of telecommunication networks, Geneva, March 2018.
[2] ITU-T Recommendation G.8271.1/Y1366.1, Network limits for time synchronization in packet networks, Geneva, March 2018.
[3] ITU-T Q13/15 document WDeTSS, Assumptions Regarding HRMs and Parameters for Initial Simulations for Time Transport via PTP using eEECs, ePRTCs, and Class C T-BCs, TD (WP3) 313, Geneva, October 2018.
[4] ITU-T Recommendation G.781, Synchronization layer functions, Geneva, August 2017.

## Slide 17: References – 2
[5] ITU-T Recommendation G.8275.1, Precision time protocol telecom profile for phase/time synchronization with full timing support from the network, Geneva, June 2016.
[6] ITU-T Supplement G.Suppl.sim, Simulations of transport of time over packet networks, Geneva, publication expected in 2018.
[7] ITU-T Recommendation G.8273.2, Timing characteristics of telecom boundary clocks and telecom time slave clocks, Geneva, August 2017.
[8] IEEE Std 1588TM – 2008, IEEE Standard for a Precision Clock Synchronization Protocol for Networked Measurement and Control Systems, 24 July 2008.

## Slide 18: Backup

## Slide 19: Simulation Model
Enhanced SyncE noise accumulation modeled separately from TE accumulation with PTP
  SyncE noise accumulation modeled as chain of 2nd-order PLLs
  SyncE noise files saved, and used in various PTP simulations
Discrete event simulation for PTP TE accumulation
  Models sending and receiving of Sync, Delay_Req, and Delay_Resp messages
  One-step behavior modeled, as small TE performance difference between one-step and two-step
  All T-BC and T-TSC filters are updated between each pair of successive discrete events, using discrete time models for 2nd-order PLLs
Results due to random noise and timestamp granularity based on 300 independent replications of each simulation case
Results for transient analyses based on single replications, because transient behavior is largely deterministic
See [6] for more details on simulation model (and also descriptions and results for cases with non-enhanced clocks)

## Slide 20: eHRMa Results – Random Effects
2 ns timestamp granularity
0.1 Hz T-BC and T-TSC filter

## Slide 21: eHRMa Results – Random Effects
4 ns timestamp granularity
0.1 Hz T-BC and T-TSC filter

## Slide 22: eHRMc Results – Random Effects
2 ns timestamp granularity
0.1 Hz T-BC and T-TSC filter

## Slide 23: eHRMc Results – Random Effects
4 ns timestamp granularity
0.1 Hz T-BC and T-TSC filter

## Slide 24: eHRMa Results – Random Effects
2 ns timestamp granularity
0.05 Hz T-BC and T-TSC filter

## Slide 25: eHRMa Results – Random Effects
4 ns timestamp granularity
0.05 Hz T-BC and T-TSC filter

## Slide 26: eHRMa Results – Random Effects
8 ns timestamp granularity
0.05 Hz T-BC and T-TSC filter

## Slide 27: eHRMc Results – Random Effects
2 ns timestamp granularity
0.05 Hz T-BC and T-TSC filter

## Slide 28: eHRMc Results – Random Effects
4 ns timestamp granularity
0.05 Hz T-BC and T-TSC filter

## Slide 29: eHRMc Results – Random Effects
8 ns timestamp granularity
0.05 Hz T-BC and T-TSC filter

## Slide 30: eHRMa Results – SyncE transient
No mitigation by turning off T-BC filtering
8 ns timestamp granularity
No measurement filter

## Slide 31: eHRMa Results – SyncE transient
No mitigation
8 ns timestamp granularity
0.1 Hz high-pass measurement filter

## Slide 32: eHRMa Results – SyncE transient
Mitigation by turning off T-BC filtering
8 ns timestamp granularity
No measurement filter

## Slide 33: eHRMa Results – SyncE transient
Mitigation by turning off T-BC filtering
8 ns timestamp granularity
0.1 Hz high-pass measurement filter

## Slide 34: Stability Consideration with Mitigation – 1
<meanPathDelay> and <offsetFromMaster> given by
  <meanPathDelay> = [(T4 – T1) – (T3 – T2)]/2
  <offsetFromMaster> = [Time on Slave (before time update) – [Time on Master]
Then
  <offsetFromMaster> = [Time on Slave] – [T1 + <meanPathDelay>] = [(T2 –T1) – (T4 – T3)]/2
IEEE Std 1588 – 2008 specifies a) and b) above, but does not specify the computational details beyond that
The computation must be organized such that the resulting algorithm is stable

## Slide 35: Stability Consideration with Mitigation – 2
Case 1
  Slave computes <meanPathDelay> after receiving Delay_Resp from master
  Slave computes <offsetFromMaster> after receiving Sync (and Follow_Up if two-step) from master, using most recently computed <meanPathDelay>
  In this case
    <meanPathDelay>(n) = [(T4(n) – T1(n)) – (T3(n) – T2(n-1))]/2
    <offsetFromMaster>(n+1) = [Time on Slave](n+1) – [T1(n+1) + <meanPathDelay>(n)
  In <meanPathDelay>(n), the term T3(n) – T2(n-1) can include the effect of a time update at the Slave between these two times
    If the T-BC filter is turned off (or if there is no filtering), this can become unstable
  Instead, the Case 2 computation on the next slide should be used

## Slide 36: Stability Consideration with Mitigation – 3
Case 2
  Figure is repeated from previous slide for convenience
  Slave computes <meanPathDelay> after receiving Delay_Resp from master
  However, now slave computes <offsetFromMaster> after receiving Delay_Resp
  In this case
    <meanPathDelay>(n) = [(T4(n) – T1(n)) – (T3(n) – T2(n))]/2
    <offsetFromMaster>(n+1) = [Time on Slave](n+1) – [T1(n+1) + <meanPathDelay>(n)
  Now in <meanPathDelay>(n), the term T3(n) – T2(n) does not include the effect of a time update at the Slave
    The resulting algorithm is stable, even if the T-BC filter is turned off