## Slide 1
.
Power Utilities are migrating to digital, fully automated substations connected by means of optical Ethernet networks. The IEC 61850 standard defines a set of Ethernet-based protocols, such as GOOSE and SV to transport critical data that requires accurate timing that can be provided by PTP that has also been adopted by this industry.
Timing Convergence in Power Utilities

## Slide 2
The new Smart Power Grid
Smart Grid require a Telecom Data Network to communicate all the elements of the Power System, including Generation plants, Substations and Customers in order to increase the efficiency, resilience and quality of the power grid, while allowing advanced management.
Timing Convergence refers to the adoption of Ethernet-based protocols such as PTP and NTP to satisfy the demand of Synchronization in an available, accurate, reliable and standard way.
PTP
GOOSE
GOOSE
Datacom
E1-T1
VoIP
SV
C-Ethernet
C-Ethernet MPLS-TP
MMS
Distribution
Generation
Customers
Substation
Customers
Distribution
Transmission
Internet
Substation
Data Network
Measuring and Control points
© 2020 ALBEDO Telecom - All rights reserved

## Slide 3
©
Substations are the building blocks of the grid.
Automation refers to the massive use of data and communications to assure the stability, efficiency and integrity of the power Service.
IEC-61850 facilitates the automation and interoperability of intelligent devices by means of standard protocols to configure, control, synchronize, transmit data, measure, and protect the grid.
The IEC 61850 in the Substation
SNTP
MMS
UDP
IP
SV
GOOSE
PTP
Ethernet
Time Sync
Control
TCP
Applications
Time Sensitive
PRP-HSR (fault-tolerant)
I E C - 6 1 8 5 0
Time Critical

## Slide 4
© 2020 ALBEDO Telecom - All rights reserved
VT CT
CB
NTP clock
PTP Master
ALBEDO
E1-T1
C37.94
SONET
SONET
Internet
Control
Copper
Events Recording
0 - Substation Evolution
Process
Station
Bay
MMI, Control Board
Copper
Protection Relays
Copper
Datacomms
Ethernet
Gateway
Relay
IED
MPLS-TP
Station Bus IEC 61850-8-1
Process Bus IEC 61850-8-2
Station Bus IEC 61850-8-1
F.O.
Copper
F.O.
F.O.
F.O.
SV
Proprietary Bus
Station clock
E1-T1
C37.94
Gateway
GOOSE, MMS
VoIP
VT CT
Metering
Switch Gear
SCADA
HMI
SNTP, PTP
PTP
SCADA
LAN A
LAN B
SNTP
PRP
PTPoPRP
IED
Control
Hardwired Protection Relay
IRIG-B
IRIG-B
SNTP
GNSS
Timing
Timing
GNSS
VT CT
Metering
Switch Gear
VT CT
Metering
Switch Gear
MU
GOOSE
S U B S T A T I O N - 1
Legacy
S U B S T A T I O N - 2
Conventional
S U B S T A T I O N - 3
Digital
S U B S T A T I O N - 4
Smart Grid
GNSS SCADA

## Slide 5: 1-2 – Test in Legacy-Conventional substations
SONET
Control
Copper
Events Recording
Protection Relays
Datacomms
Proprietary Bus
E1-T1
C37.94
HMI
SCADA
IRIG-B
Timing
VT CT
Metering
Switch Gear
What to Test
Serial communication data: RS-232, RS-422, V.35, V.36
IRIG-B: timing
E1 / T1: pulse, voice, data
C37.94: one-way / two-way delays, event emulations
Teleprotection: One-way delay
Ethernet capacity/quality: RFC 2544, eSAM, etc.
PHM
RJ45-C
BNC-C
SFP+ A
SFP+ B
RJ45-A
RJ45-B
SFP-A
Micro SD
SMB-2
SMB-1
SMA
SMB-C
RJ45
SFP-B
xGenius testing interfaces
Objectives
Check and adjust teleprotection based on C37.94
Check the quality of the Ethernet network
Testing
Points
Process
Station
Bay

## Slide 6: 3 – Test in Digital Substations
NTP clock
E1-T1
C37.94
SONET
Ethernet
Gateway
Relay
IED
Station Bus IEC 61850-8-1
F.O.
Copper
F.O.
SCADA
SNTP
SNTP
GNSS
VT CT
Metering
Switch Gear
What to Test
Serial communication data: RS-232, RS-422, V.35, V.36
IRIG-B: timing
E1 / T1: pulse, voice, data
Ethernet: RFC 2544, eSAM, etc.
IP: ping, trace route
Fiber Optic: Power, OTDR
NTP: message, delays, jitter, TE
Teleprotection: C37.94, One-way delay, Quality
Testing
Points
Objectives
Check the teleprotection times C37.94
Check and adjust IRIG-B and NTP synchronisms
Check the quality of the Ethernet network
Install and maintain fiber optics
Process
Station
Bay
PTP/NTP clock

## Slide 7: 4 – Test in IEC-61850 Substations
CB
PTP Master
Ethernet
1.......p....p....s / TOD 17:23UTC
ALBEDO
Internet
MPLS-TP
Process Bus IEC 61850-8-2
Station Bus IEC 61850-8-1
F.O.
F.O.
SV
Station clock
Gateway
GOOSE, MMS
VoIP
SNTP, PTP
PTP
LAN A
LAN B
PRP
PTPoPRP
IED
GNSS
MU
GOOSE
What to Test
Serial communication data: RS-232, RS-422, V.35, V.36
IRIG-B: time
E1 / T1: pulse, voice, data
C37.94: delays, event emulations
Teleprotection: Unilateral delay
Ethernet: RFC 2544, eSAM, etc.
IP: ping, tracking route
MPLS-TP
Fiber Optic: Power, OTDR
NTP: message, delays, jitter, TE
PTP: Wander, PPS, TE
GOOSE: analysis / capture / decoding
SV: analysis / capture / decoding
MMS: analysis / capture / decoding
Master / slave clock emulation
IEC-61850: delay of protocols
Objectives
Guarantee the interconnection between different manufacturers
Interconnection of new and old PTP-NTP-IRIG-B synchronism
Install and develop new protocols like GOOSE
Testing
Points
Process
Station
Bay

## Slide 8
PTP Timing Analysis
TE chronograph
TE analysis (PASS/FAIL)
Objectives
Acceptance (IEDs, TCs, GMs, SCs…)
Bringing into service
Maintenance and troubleshooting
Performance monitoring
Tests
Performance in locked mode
Reference switchover test
Holdover performance
Interoperability with Power / Utility profiles
TC testing
Performance Metrics
TE or TIE
Frequency offset and drift
Delay and delay asymmetry
© 2020 ALBEDO Telecom - All rights reserved

## Slide 9: PTP testing in Power Utility Applications
Three different PTP Profiles
IEEE C37.238 (2011), “Power profile”
IEEE C37.238 (2017), “Power profile”
ISO/IEC 61850-9-3, “Utility profile”
Some particularities
Peer-to-peer delay mechanism
Paralel Redundancy Protocol (PRP)
“Special” TLVs: ATOI, C37.238 extension
PTP Telecom profiles and NTP used very often
© 2021 ALBEDO Telecom - All rights reserved
1.......p....p....s / TOD 17:23UTC
LAN A
PTP GM
IED (PTP SC)
LAN B
PRP
PTP GM
IED (PTP SC)
TC
TC
Peer Delay Request / Response
Peer Delay Request / Response
Peer Delay Request / Response

## Slide 10
NTP testing
Testing features
NTPv3 / v4 server and client emulation
Traffic filtering, classification, analysis
NTP delay and asymmetry
Statistics of Time Error (TE)
Client
Offset: difference between clocks
Stratum 2, 3
Offset = 5’
Stratum 2, 3
IP
NTP Server
Stratum 1
IP
IP
Objectives
The same that for PTP
Client
NTP Server
Client
NTP Server
Stratum 1

## Slide 11: IRIG-B testing
  IRIG-B sends a timing signal every second at 100 pulse/sec rate therefore the 100 is the number of bits of each frame. IRIG-B info includes Year, Day, Hour, Min, Sec.
      AM modulated clock reference input and output
      Unmodulated (DCLS) i/o over RS-422 / RS-485 or TTL
      Manchester encoded IRIG-B input and output
Test & Measurement
Analysis of the received IRIG-B frame
Events: Leap seconds, Time Zones, DST…
Timing accuracy: Timestamp decoding, Time Scale, Time Error
IRIG - Xabc
1: AM (Amplitude Modulated)
A: 1000 PPS
> IRIG-B: 100 PPS <
D: 1 PPM
E: 10 PPS
G: 10000 PPS
H: 1 PPS
Rate
Carrier
Modulation
Coding
2: Manchester Modulated
0: BCD, CF, SBS
1: BCD, CF
2: BCD
3: BCD, SBS
4, 5, 6, 7: others
0: No carrier (DCLS) 1: 100 Hz
2: 1 kHz
3: 10 kHz
4: 100 kHz
5: 1 MHz
0: Unmodulated DCLS
BCD - Binary Coded Decimal, coding of time (HH,MM,SS,DDD) SBS - Straight Binary Second of day (0....86400)
CF - Control Functions depending on the user application
DCLS B000
AM B120
MANCHESTER B220
BCD 0000 = 0
0001 = 1
0010 = 2
0011 = 3
0100 = 4
0101 = 5
0110 = 6
0111 = 7
1000 = 8
1001 = 9
IRIG SAMPLES: B000, B120, B220
IRIG-B
© 2020 ALBEDO Telecom - All rights reserved

## Slide 12: Delay and Asymmetry assurance
Testing Delay Modes
Bidirectional Delay (Round-Trip Delay)
One way delay with GNSS or ToD help Latency results
Bidirectional Delay or Round-Trip Delay (RTD)
One Way Delay Forward and Reverse Path
Asymmetry with min. / max records
Patch cord delay compensation
PASS / FAIL indication
Objectives
Bidirectional Delay or Round-Trip Delay (RTD)
S U B S T A T I O N - 1
S U B S T A T I O N - 2
IED
Latency < 2 ms Latency < 10ms Latency < 2 ms
© 2020 ALBEDO Telecom - All rights reserved

## Slide 13: Capture & Analysis of GOOSE packets
Station
Bay
Process
VT CT
SV
IED-1
Measures
IED-2
Protection
IED-3
Control
Primary Power
GOOSE-1
Station Bus IEC 61850-8-1
MU
GOOSE-1
CB
GOOSE-2
GOOSE-2
GOOSE-2
SV GOOSE-2
GOOSE is a messaging system used by IEDs and mission-critical applications to report substation events: commands, alarms, indications, measurements
Objectives
Decoding of faults in GOOSE protocol
Facilitate interconnection between manufacturers
Verify and adjust the latency of GOOSE packets